OVERHEAD LINE CONDUCTORS

Oman aluminum processing industries LLC (OAPIL) is a joint venture between two of the prominent companies in Oman; Oman Cables Industry (SAOG) and Takamul investments company (SAOC).Oman cables, a Muscat securities market listed company, is a leading supplier of electrical power Cables in the global markets.Oman Cables is an associate company of Netherlands based Draka, the third largest power and communications Cable manufacture in Europe with operations in more than 60 countries.

Takamul investment company is a subsidiary of Oman Oil Company (SAOC). Takamul has the responsibility of developing downstream industries in Metals, Petro Chemicals and Minerals in

the Sultanate of Oman.

OAPIL  was established in February 2008 and has started its state of the art manufacturing

Oman Aluminum Processing Industries LLC (OAPIL)

Established to meet the fast growing requirements of the power sector in the Middle East, Africa and the Indian subcontinent region, OAPIL positions itself as a credible and high quality player with the latest technology and is poised to deliver superior quality of products at great value.

facilities down stream to Sohar Aluminum Company (SAC), a newly built built smelter in Sohar ,Oman. OAPIL receives liquid aluminum from SAC to produce electrical grade Aluminum Rods which are processed further to manufacture Overhead line conductors (OHLC) for Electrical Power transmission.

The equipment an technology for manufacture of Aluminum Rods has been secured from Southwire USA. The equipments of OHLC manufacturing have been hand picked from reputed europian suppliers. The state-of-the-art technology enables OAPIL to add immense value to customers' business .

OAPIL is committed to meet the growing needs of the electricity sector in Oman,

Other GCC Countries and specific international markets.  OAPIL purposes to meet diverse and exacting needs of power utilities and international EPC majors with superior quality of its value added products and services.

OVERHEAD LINE CONDUCTORS

OVERHEAD LINE CONDUCTORS

Contents

Message

AAC -   AII Aluminium Conductors

* British Sizes

* British Sizes

* IEC Sizes

* American Sizes

* Canada Sizes

* German Sizes

* Oman Sizes

ACSR – Aluminium Conductor Steel Reinforced

* British  Sizes

*  British  Sizes

*  IEC  Sizes

* American Sizes

*  Canadian Sizes

*  Germen Sizes

AAAC- AII Aluminium ALLoy Conductors

* British Sizes

* IEC Sizes

* American Sizes

* Canadian Sizes

* German Sizes

PVC Coverd Copper Conductors

* British Sizes

BS 215

BS EN 50182

IEC 61089

ASTM B 231

CSA C 49

DIN 48 201

OES 25D

BS 215

BS EN 50182

IEC 61089

ASTM B 231

CSA C 49

DIN 48 204

BS EN 50182

IEC 1089

ASTM B 399

CSA C 49

DIN 48 201

BS 7884

1

5-11

6

6

7

8

9

10

11

13-20

14

14

15

16-17

18-19

20

21-26

22

23

24

26

26

27-28

28

OVERHEAD LINE CONDUCTORS

All  -   ALUMINUM CONDUCTORS

AAC

All-aluminum conductors are the most favoured type for use in the construction of relatively short span distribution schemes in common use on lines for voltage up to 60kv.

Another frequent application for all-aluminum conductors is in flexible busbar connections. Although aluminum –to-copper connections can be made, it is better to use aluminum conductors for service connections as various forms of covered cables are available for this purpose.

The date sheets show the most common sizes of conductor but other size, any recognized standards or customer specification can also be required.

AAC insulated with XPLE of PVC can also be supplied as per customers' requirements.

BRITISH SIZES

ACC

All  -   ALUMINUM CONDUCTORS

BS 215 : Part 1 : 1970                                            Table 1A

OVERHEAD LINE CONDUCTORS

| Code name | Nominal Area 2 | Stranding & Wife Diameter | Approximate Overall Diameter | Total Area 2 | Approximate Weight | Breaking Load | DC Resistance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | mm | mm | mm | Kg/Km | Kn | Ohm/km | A |
| Midge | 22 | 7/2.06 | 6.18 | 23.33 | 64 | 3.99 | 1.22700 | 114 |
| Ant | 50 | 7/3.10 | 9.30 | 52.83 | 145 | 8.28 | 0.54190 | 181 |
| Fly | 60 | 7/3.40 | 10.20 | 63.55 | 174 | 9.90 | 0.45050 | 199 |
| Wasp | 100 | 7/4.39 | 13.17 | 106.00 | 290 | 16.00 | 0.27020 | 271 |
| Hornet | 150 | 19/3.25 | 16.25 | 157.60 | 434 | 25.70 | 0.18250 | 346 |
| Chafer | 200 | 19/3.78 | 18.90 | 213.20 | 587 | 32.40 | 0.13490 | 414 |
| cockroach | 250 | 19/4.22 | 21.10 | 265.70 | 731 | 40.40 | 0.10830 | 470 |
| Butterfly | 300 | 19/4.65 | 23.25 | 322.70 | 888 | 48.75 | 0.08916 | 528 |
| Centipede | 400 | 37/3.78 | 26.46 | 415.20 | 1145 | 63.10 | 0.06944 | 619 |

BS EN 50182 : 2001

TABLE 1B

| Code name | Nominal Area | Stranding & Wife Diameter | Approximate Overall Diameter | Total Area | Approximate Weight | Breaking Load | DC Resistance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | mm | mm | mm | Kg/Km | Kn | Ohm/km | A |
| Gnat | - | 7/2.21 | 6.63 | 26.9 | 73 | 4.83 | 1.0643 | 124 |
| Mosquito | - | 7/2.59 | 7.77 | 36.9 | 101 | 6.27 | 0.7749 | 144 |
| Ladybird | - | 7/2.79 | 8.37 | 42.8 | 117 | 7.28 | 0.6678 | 159 |
| Bluebottle | - | 7/3.66 | 10.98 | 73.6 | 201 | 11.78 | 0.3880 | 219 |
| Earwig | - | 7/3.78 | 11.34 | 78.6 | 215 | 12.57 | 0.3638 | 227 |
| Grasshopper | - | 7/3.91 | 11.73 | 84.1 | 230 | 13.46 | 0.3400 | 238 |
| Clegg | - | 7/4.17 | 12.51 | 95.6 | 261 | 15.30 | 0.2989 | 256 |
| Beetle | - | 19/2.67 | 13.35 | 106.4 | 292 | 18.08 | 0.2701 | 274 |
| Bee | - | 7/4.90 | 14.70 | 132.0 | 361 | 21.12 | 0.2165 | 308 |
| Catterpillar | - | 19/3.53 | 17.65 | 185.9 | 511 | 29.75 | 0.1546 | 380 |
| Spider | - | 19/3.99 | 19.95 | 237.6 | 653 | 38.01 | 0.1210 | 439 |
| Moth | - | 19/5.00 | 25.00 | 373.1 | 1025 | 59.69 | 0.0770 | 572 |
| Drone | - | 37/3.58 | 25.06 | 372.4 | 1027 | 59.59 | 0.0774 | 572 |
| Maybug | - | 37/4.09 | 28.63 | 486.1 | 1340 | 77.78 | 0.0593 | 676 |
| Scorpion | - | 37/4.27 | 29.89 | 529.8 | 1461 | 84.77 | 0.0544 | 710 |
| Cicada | - | 37/4.65 | 32.55 | 628.3 | 1732 | 100.54 | 0.0459 | 784 |

All-ALUMINIUM CONDUCTORS

IEC : 61089 (1991-06)                                          TABLE 2

IEC SIZES

AAC

OVERHEAD LINE CONDUCTORS

| Code Name | National Area | Stranding & Wife Diameter | Approximate Overall Diameter | Approximate Weight | Breaking Load | DC Resistance at 20 C |
| --- | --- | --- | --- | --- | --- | --- |
|  | mm | mm | mm | Kg / km | kN | Ohm/km |
| 10 | 10 | 7/1.35 | 4.05 | 27.4 | 1.95 | 2.8633 |
| 16 | 16 | 7/1.71 | 5.12 | 43.8 | 3.04 | 1.7896 |
| 25 | 25 | 7/2.13 | 6.40 | 68.4 | 4.50 | 1.1453 |
| 40 | 40 | 7/2.70 | 8.09 | 109.4 | 6.80 | 0.7158 |
| 63 | 63 | 7/3.39 | 10.20 | 172.3 | 10.39 | 0.4545 |
| 100 | 100 | 19/2.59 | 12.90 | 274.8 | 17.00 | 0.2877 |
| 125 | 125 | 19/2.89 | 14.50 | 343.6 | 21.25 | 0.2302 |
| 160 | 160 | 19/3.27 | 16.40 | 439.8 | 26.40 | 0.1798 |
| 200 | 200 | 19/3.66 | 18.30 | 549.7 | 32.00 | 0.1439 |
| 250 | 250 | 79/4.09 | 20.50 | 687.1 | 40.00 | 0.1151 |
| 315 | 315 | 37/3.29 | 23.00 | 867.9 | 51.97 | 0.0916 |
| 400 | 400 | 37/3.71 | 26.00 | 1102.0 | 64.00 | 0.0721 |
| 450 | 450 | 37/3.94 | 27.50 | 1239.8 | 72.00 | 0.0641 |
| 500 | 500 | 37/4.15 | 29.00 | 1377.6 | 80.00 | 0.0577 |
| 560 | 560 | 37/4.39 | 30.70 | 1542.9 | 89.60 | 0.0515 |
| 630 | 630 | 61/3.63 | 32.60 | 1738.3 | 100.80 | 0.0458 |
| 710 | 710 | 61/3.85 | 34.60 | 1959.1 | 113.60 | 0.0407 |
| 800 | 800 | 61/4.09 | 36.80 | 2207.4 | 128.00 | 0.0361 |
| 900 | 900 | 61/4.33 | 39.00 | 2483.3 | 144.00 | 0.0321 |
| 100 | 100 | 61/4.57 | 41.10 | 2759.2 | 160.00 | 0.0289 |
| 1120 | 1120 | 91/3.96 | 43.50 | 9093.5 | 179.20 | 0.0258 |
| 1250 | 1250 | 91/4.18 | 46.00 | 3452.6 | 200.00 | 0.0231 |
| 1400 | 1400 | 91/4.43 | 48.70 | 3866.9 | 224.00 | 0.0207 |
| 1500 | 1500 | 91/4.58 | 50.40 | 4143.1 | 240.00 | 0.0193 |

AAC

All-ALUMINIUM CONDUCTORS

ASTM B 231-90 (Class A and Class AA)               Table 3

AMERICAN SIZES

OVERHEAD LINE CONDUCTORS

| Code Name | Total Area |  | Stranding and wire Diameter | Approximate Overall Diameter | Weight | Breaking Load | DC Resisance at 20 C | Current Rating |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | AWG or MCM | mm | mm | mm | Kg/km | kN | Ohm/km |  | A |
| Peachbell | 6.0 | 13.30 | 7/1356 | 4.68 | 36.6 | 2.53 | 2.1690 |  | 72 |
| Rose | 4.0 | 21.10 | 7/1.96 | 5.88 | 58.2 | 9391 | 1.3620 |  | 104 |
| Iris | 2.0 | 66.60 | 7/2.47 | 7.41 | 92.6 | 5.99 | 0.8574 |  | 136 |
| Pansy | 1.0 | 42.40 | 7/2.78 | 8.34 | 116.6 | 7.30 | 0.6801 |  | 157 |
| Poppy | 1/0.0 | 53.50 | 7/3.12 | 9.36 | 147.2 | 8.84 | 0.5390 |  | 180 |
| Aster | 2/0.0 | 67.40 | 7/3.50 | 10.50 | 185.7 | 11.10 | 0.4276 |  | 207 |
| Phlox | 3/0.0 | 85.00 | 7/3.93 | 11.79 | 233.9 | 13.50 | 0.3390 |  | 237 |
| Oxlip | 4/0.0 | 107.20 | 7/4.42 | 13.26 | 295.2 | 17.00 | 0.2688 |  | 273 |
| Valerian | 250.00 | 126.70 | 19/2.91 | 14.55 | 348.6 | 20.70 | 0.2275 |  | 305 |
| Sneezewort | 250.00 | 126.70 | 7/4.80 | 14.40 | 348.8 | 20.10 | 0.2275 |  | 300 |
| Laurel | 266.80 | 135.20 | 19/3.10 | 15.05 | 372.2 | 22.10 | 0.2133 |  | 317 |
| Daisy | 266.80 | 135.20 | 7/4.96 | 14.88 | 372.3 | 21.40 | 0.2133 |  | 313 |
| Peony | 300.00 | 152.00 | 19/3.19 | 15.95 | 418.3 | 24.30 | 0.1896 |  | 340 |
| Tulip | 336.40 | 170.50 | 19/3.38 | 16.90 | 469.5 | 27.30 | 0.1695 |  | 364 |
| Daffodil | 350.00 | 177.30 | 19/3.45 | 17.25 | 487.9 | 28.40 | 0.1625 |  | 373 |
| Canna | 397.50 | 201.40 | 19/3.67 | 18.35 | 554.9 | 31.60 | 0.1432 |  | 401 |
| Goldentuft | 450.00 | 228.00 | 19/3.91 | 19.55 | 627.6 | 35.00 | 0.1264 |  | 432 |
| Syringa | 477.00 | 242.00 | 37/2.88 | 20.16 | 664.8 | 38.60 | 0.1193 |  | 449 |
| Cosmos | 477.00 | 242.00 | 19/4.02 | 20.10 | 664.8 | 37.00 | 0.7793 |  | 447 |
| Hyacinth | 500.00 | 253.30 | 37/2.95 | 20.65 | 696.8 | 40.50 | 0.1137 |  | 461 |
| Zinnia | 500.00 | 253.30 | 19/4.12 | 20.60 | 697.1 | 38.90 | 0.1137 |  | 459 |
| Dehlia | 556.50 | 252.00 | 19/4.35 | 21.75 | 445.8 | 43.30 | 0.1023 |  | 489 |
| Mistletoe | 556.50 | 282.00 | 37/3.12 | 21.84 | 775.7 | 44.30 | 0.1023 |  | 493 |
| Meadowsweet | 600.00 | 304.00 | 37/3.23 | 22.61 | 836.3 | 47.50 | 0.0948 |  | 513 |
| Orchid | 636.00 | 323.30 | 37/3.33 | 23.30 | 886.9 | 50.40 | 0.089. |  | 531 |
| Heuchera | 650.00 | 329.40 | 37/3.37 | 23.59 | 907.4 | 51.70 | 0.0875 |  | 538 |
| Flag | 700.00 | 354.70 | 61/2.72 | 24.48 | 978.8 | 57.10 | 0.0813 |  | 563 |
| Varbena | 700.00 | 354.70 | 37/3.49 | 24.43 | 978.7 | 55.40 | 0.0813 |  | 562 |
| Nasturtium | 715.50 | 362.60 | 61/2.75 | 24.75 | 998.5 | 58.40 | 0.0795 |  | 570 |
| Voilet | 715.50 | 362.60 | 37/3.5. | 24.71 | 998.5 | 56.70 | 0.0795 |  | 570 |
| Cattail | 750.00 | 380.00 | 67/2.82 | 25.38 | 1046.0 | 60.30 | 0.0759 |  | 586 |
| Petunia | 750.00 | 380.00 | 37/3.62 | 25.34 | 1046.0 | 58.60 | 0.0759 |  | 585 |
| Lilac | 795.00 | 402.80 | 61/2.90 | 26.10 | 1110.0 | 63.80 | 0.0715 |  | 607 |
| Arbutus | 795.00 | 402.80 | 37/3.72 | 26.04 | 1109.0 | 61.80 | 0.0725 |  | 605 |
| Snapdragon | 900.00 | 456.00 | 61/3.09 | 27.81 | 1256.0 | 70.80 | 0.0632 |  | 653 |
| Cockscomb | 900.00 | 456.00 | 37/3.96 | 27.72 | 1256.0 | 68.40 | 0.0632 |  | 651 |
| Goldenrod | 954.00 | 483.40 | 61/3.18 | 28.62 | 1331.0 | 75.00 | 0.0596 |  | 675 |
| Mangnolia | 954.00 | 483.40 | 37/4.08 | 28.56 | 1331.0 | 72.60 | 0.0596 |  | 674 |
| Camelia | 1000.0 | 506.70 | 61/3.25 | 29.25 | 1394.0 | 75.30 | 0.0569 |  | 693 |
| Hawkweed | 1000.00 | 506.70 | 37/7.18 | 29.26 | 1395.0 | 76.20 | 0.0596 |  | 693 |
| Larkspur | 1033.50 | 523.70 | 61/3.37 | 29.79 | 1442.0 | 81.30 | 0.0550 |  | 707 |
| Bluebell | 1033.50 | 523.70 | 37/4.25 | 29.75 | 1441.0 | 78.80 | 0.0500 |  | 786 |
| Marigold | 1113.00 | 564.00 | 61/3.43 | 30.87 | 1553.0 | 87.30 | 0.0577 |  | 738 |
| Hawthorn | 1192.50 | 604.20 | 61/3.55 | 31.95 | 4662.0 | 93.50 | 0.0477 |  | 767 |
| Narcissus | 1272.00 | 644.50 | 61/3.67 | 33.03 | 1774.0 | 98.10 | 0.0447 |  | 797 |
| Columbine | 1351.00 | 694.80 | 61/3.78 | 34.02 | 1884.0 | 104.00 | 0.0421 |  | 825 |
| Carnation | 1431.00 | 725.10 | 61/3.89 | 35.01 | 1997.0 | 108.00 | 0.0398 |  | 854 |
| Gladiolus | 1510.50 | 765.41 | 61/4.00 | 36.00 | 2108.0 | 114.00 | 0.0376 |  | 881 |
| Coreopsis | 1590.00 | 805.70 | 61/4.10 | 36.90 | 2216.0 | 120.00 | 0.0358 |  | 907 |
| Jessamine | 1750.00 | 886070 | 61/4.30 | 38.70 | 2442.0 | 132.00 | 0.0325 |  | 959 |
| Cwslip | 2000.00 | 1013.00 | 91/3.77 | 41.47 | 2787.0 | 153.00 | 0.0284 |  | 1035 |
| Sagebrush | 2250.00 | 1140.00 | 91/3.99 | 43.89 | 3166.0 | 167.00 | 0.0255 |  | 1108 |
| Lupine | 2500.00 | 1267.00 | 91/4.21 | 46.31 | 3519.0 | 186.00 | 0.0230 |  | 1178 |
| Bitterroot | 2750.00 | 1393.00 | 91/4.42 | 48.62 | 3872.0 | 205.00 | 0.0209 |  | 1242 |
| Trillium | 3000.00 | 1520.00 | 127/3.90 | 50.70 | 4226.0 | 223.00 | 0.0191 |  | 1308 |
| Bluebonnet | 3500.00 | 1773.00 | 127/4.22 | 54.86 | 4977.0 | 261.00 | 0.0166 |  | 1425 |

CANADIAN SOZES

AAC

AII – ALUMINIUM CONDUCTORS

CSA C  49 – 1965                                                Table 4

OVERHEAD LINE CONDUCTORS

| Code Name | Total Area | Stranding and Wire Diameter | Approimate Overall Diameter | Weight | Breaking Load | DC Resisstance at 20 C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | mm | mm | Kg/km | Kn | Ohm/km | A |
| Rose Lily Iris Pansy Poppy Aster Phlox Oxlip Daisy Valerian Laurel Peony Tulip Daffodil Canna - Goldentuft Cosmos Zinnia Delhia - Meadowsweet Orchid Heuchhera Varbena Voilet Patunia Arbutus - Anemone Cockscomb Magnolia Hawkweed Bluebell - Marigold Hawthorn - Narcissus - Columbine - Carnation - Gladiolus Corepsis - - - | 21.16 26.65 33.61 42.39 53.48 67.42 85.03 107.23 135.16 126.71 135.16 152.00 170.45 177.35 201.42 202.71 228.00 241.68 253.35 282.00 278.71 304.00 322.26 329.35 354.71 362.58 380.00 402.84 405.35 443.10 456.06 483.42 506.71 523.68 557.35 563.93 604.26 608.06 644.51 658.71 684.84 709.42 725.10 760.06 765.35 805.68 810.71 861.42 912.06 | 7/1.961 7/2.202 7/2.474 7/2.776 7/3.119 7/3.503 7/3.932 7/4.417 7/4.960 19/2.913 19/3.010 19/3.193 19/3.381 19/3.447 19/3.673 19/3.686 19/3.909 19/43023 19/4.120 19/4.346 37/3.096 37/3.233 37/3.330 37/3.366 37/3.493 37/3.533 37/3.617 37/3.724 37/3.734 37/3.904 37/3.962 37/4.079 37/4.176 37/4.244 61/3.411 61/3.432 61/3.551 61/3.564 61/3.668 61/3.708 61/3.780 61/3.848 61/3.891 61/3.983 61/3.998 61/4.096 61/4.115 61/4.239 91/3.571 | 5.89 6.61 7.42 8.33 9.36 10.51 11.80 13.25 14.90 14.57 15.05 15.97 16.91 17.27 18.36 18.43 19.55 20.12 20.60 21.73 21.67 22.63 23.31 23.56 24.45 24.74 25.32 26.06 263.14 27.33 27.73 28.55 29.23 29.72 30.70 30.89 31.95 32.08 33.02 33.37 34.01 34.63 35.03 35.85 35.99 36.91 37.04 38.15 39.28 | 58 73 92 116 146 184 232 293 369 348 372 417 467 488 554 558 626 664 695 774 768 838 888 908 978 1000 1048 1112 1118 1222 1257 1333 1396 1445 1539 1559 1670 1679 1781 1818 1893 1958 2004 2098 2116 2226 2238 2378 2521 | 4.1 5.0 6.2 7.6 9.2 11.6 14.1 17.7 22.4 22.3 23.8 26.2 29.4 30.6 34.0 34.2 37.7 40.0 41.9 46.7 48.0 52.4 55.6 56.8 61.1 62.5 64.2 68.1 68.5 73.3 75.4 80.0 83.8 86.6 96.1 97.2 104.1 102.7 108.8 111.2 115.6 117.4 119.9 125.7 126.5 133.2 134.1 142.6 153.9 | 1.3510 1.0720 0.8497 0.6739 0.5341 0.4236 0.3360 0.2664 0.2113 0.2274 0.2129 0.1880 0.1638 0.1624 0.1427 0.1421 0.1263 0.1188 0.1132 0.1018 0.1033 0.0948 0.0896 0.876 0.0814 0.0797 0.0758 0.0715 0.0712 0.0653 0.0633 0.0597 0.0568 0.0551 0.0518 0.0512 0.0479 0.0476 0.0450 0.0440 0.0423 0.0407 0.0400 0.0381 0.0377 0.0358 0.0358 0.0335 0.0316 | 104 124 136 157 180 207 237 273 313 305 317 340 364 373 401 402 432 447 459 489 485 513 531 538 562 570 585 605 608 641 657 675 693 706 733 738 767 771 797 807 825 842 854 877 881 907 910 942 975 |

AII-ALUMINIUM CONDUCTORS

DIN 48 201 Part 5 Apr  1982                                    Table  5

AAC

GERMAN SIZE

OVERHEAD LINE CONDUCTORS

| Area |  | Stranding and Wire Diameter | Overall Diameter | Weight | Breaking Load | DC Resisstance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal | Actual |  |  |  |  |  |  |
| mm | mm | mm | mm | Kg/km | kN | Ohm/km | A |
| 16 | 15.89 | 7/1.70 | 5.1 | 43 | 2.84 | 1.80170 | 110 |
| 25 | 24.25 | 7/2.10 | 6.3 | 66 | 4.17 | 1.18060 | 145 |
| 35 | 34.36 | 7/2.50 | 7.5 | 94 | 5.78 | 0.83320 | 180 |
| 50 | 49.48 | 7/3.00 | 9.0 | 135 | 7.94 | 0.57860 | 225 |
| 50 | 48.35 | 19/1.80 | 9.0 | 133 | 8.45 | 0.59480 | 225 |
| 70 | 65.82 | 19/2.10 | 10.5 | 181 | 11.32 | 0.43700 | 270 |
| 95 | 93.27 | 19/2.50 | 12.5 | 256 | 15.68 | 0.30840 | 340 |
| 120 | 117.00 | 19/2.80 | 14.0 | 322 | 18.78 | 0.24590 | 390 |
| 150 | 147.10 | 37/2.25 | 15.8 | 406 | 25.30 | 0.19600 | 455 |
| 185 | 181.62 | 37/2.50 | 17.5 | 500 | 30.54 | 0.15880 | 520 |
| 240 | 242.50 | 61/2.25 | 20.3 | 670 | 39.51 | 0.11920 | 625 |
| 300 | 299.40 | 61/2.50 | 22.5 | 827 | 47.70 | 0.09651 | 710 |
| 400 | 400.10 | 61/2.89 | 26.0 | 1104 | 60.86 | 0.07222 | 855 |
| 500 | 499.80 | 61/3.23 | 29.1 | 1379 | 74.67 | 0.05782 | 990 |
| 625 | 626.20 | 91/2.96 | 32.6 | 1732 | 95.25 | 0.04625 | 1140 |
| 800 | 802.10 | 91/3.35 | 36.9 | 2218 | 118.39 | 0.03611 | 1340 |
| 1000 | 999.70 | 91/3.74 | 41.1 | 2767 | 145.76 | 0.02897 | 1540 |

AAC+XLPE

OMAN SIZES

OVERHEAD LINE CONDUCTORS

XLPE CONVERED ALL ALUMIMIUM CONDUCTORS

OES  25D : jan  1995                                           Table 6

XLPE CONVERED ALL ALUMIMIUM CONDUCTORS

OES  25D : jan  1995                                           Table 6

| Nominal Area | Section Area | Stranding and Wire Diameter | Approximate Conductor Diameter | Approximate Weight | Average Insulation Thickness | Approximate Overall Diameter | UTS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| mm | mm | mm | mm | Kg/km | mm | mm | Kg |
| 35 | 37.16 | 7/2.60 | 7.80 | 101.50 | 1.2 | 10.20 | 576.0 |
| 70 | 73.65 | 7/3.66 | 10.93 | 202.77 | 1.4 | 13.78 | 1216.0 |
| 120 | 119.51 | 19/2.83 | 14.15 | 329.39 | 1.6 | 17.35 | 1991.8 |
| 200 | 213.20 | 19/3.78 | 18.90 | 587.00 | 1.8 | 22.50 | 3240.0 |

AII-ALUMINIUM CONDUCTORS STEEL REINFORCED

IEC  61089  :  `1991                                                       Table    8

ACSR

IEC SIZES

OVERHEAD LINE CONDUCTORS

| Code Number | Steel Ratio | Area |  |  | Stranding & Wire Diameter |  | Diameter |  | Approximate Weight | Breaking Load | DC resistance |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Aluminium | Steel | Total | Aluminium | Steel | Core | Conductor |  |  |  |
|  |  | mm² | mm² |  | mm² | mm | mm |  | Kg/km | kN | Ohm/km |
| 16 | 17 | 16 | 2.67 | 18.7 | 6/1.84 | 1/1.84 | 1.84 | 5.53 | 64.6 | 6.08 | 1.7934 |
| 25 | 17 | 25 | 4.17 | 29.2 | 6/2.30 | 1/2.30 | 2.30 | 6.91 | 100.9 | 9.13 | 1.1478 |
| 40 | 17 | 40 | 6.67 | 46.7 | 6/2.91 | 1/2.91 | 2.91 | 8.74 | 161.5 | 14.40 | 0.7174 |
| 63 | 17 | 63 | 10.50 | 73.5 | 6/3.66 | 1/3.66 | 3.66 | 11.00 | 254.4 | 21.63 | 0.4555 |
| 100 | 17 | 100 | 16.70 | 117.0 | 6/4.61 | 1/4.61 | 4.61 | 13.80 | 403.8 | 34.33 | 0.2869 |
| 125 | 6 | 125 | 6.94 | 132.0 | 18/2.97 | 1/2.97 | 2.97 | 14.90 | 397.9 | 29.17 | 0.2304 |
| 125 | 16 | 125 | 20.40 | 145.0 | 26/2.47 | 7/1.92 | 5.77 | 15.70 | 503.9 | 45.69 | 0.2310 |
| 160 | 6 | 160 | 8.89 | 169.0 | 18/3.36 | 1/3.36 | 3.36 | 16.80 | 509.3 | 36.18 | 0.1800 |
| 160 | 16 | 160 | 26.10 | 186.0 | 26/2.80 | 7/2.18 | 6.53 | 17.70 | 644.9 | 57.69 | 0.1805 |
| 200 | 6 | 200 | 11.10 | 211.1 | 18/3.76 | 1/3.76 | 3.76 | 18.80 | 636.7 | 44.22 | 0.1440 |
| 200 | 16 | 200 | 32.60 | 233.0 | 26/3.13 | 7/2.43 | 7.30 | 19.80 | 806.2 | 70.13 | 0.1444 |
| 250 | 10 | 250 | 24.60 | 275.0 | 22/3.80 | 7/2.11 | 6.34 | 21.60 | 880.6 | 68.72 | 0.1154 |
| 250 | 16 | 250 | 40.70 | 291.0 | 26/3.50 | 7/2.72 | 8.16 | 22.20 | 1007.7 | 87.67 | 0.1155 |
| 315 | 7 | 315 | 21.80 | 337.0 | 45/2.99 | 7/1.99 | 5.97 | 23.90 | 1039.6 | 79.03 | 0.0917 |
| 315 | 16 | 315 | 51.30 | 366.0 | 26/3.93 | 7/3.05 | 9.16 | 24.90 | 1269.7 | 106.83 | 0.0917 |
| 400 | 7 | 400 | 27.70 | 428.0 | 45/3.36 | 7/2.24 | 6.73 | 26.90 | 1320.1 | 98.36 | 0.0722 |
| 400 | 13 | 400 | 51.90 | 452.0 | 54/3.07 | 7/3.07 | 9.21 | 27.60 | 1510.3 | 123.40 | 0.0723 |
| 450 | 7 | 450 | 31.10 | 451.0 | 481.0 | 45/3.57 | 7/2.38 | 7.14 | 28.50 | 1485.2 | 107.47 |
| 450 | 13 | 450 | 58.30 | 508.0 | 54/3.26 | 7/3.26 | 9.77 | 29.30 | 1699.1 | 138.42 | 0.0643 |
| 500 | 7 | 500 | 34.60 | 535.0 | 45/3.76 | 7/2.51 | 7.52 | 30.10 | 1650.2 | 119.41 | 0.40578 |
| 500 | 13 | 500 | 64.80 | 565.0 | 54/3.43 | 7/3.43 | 10.30 | 30.90 | 1887.9 | 153.80 | 0.0578 |
| 560 | 7 | 560 | 38.70 | 599.0 | 45/3.98 | 7/2.65 | 7.96 | 31.80 | 1848.2 | 133.74 | 0.0516 |
| 560 | 13 | 560 | 70.90 | 631.0 | 54/3.61 | 19/2.18 | 10.90 | 32.70 | 1203.4 | 172.59 | 0.0516 |
| 360 | 7 | 630 | 43.60 | 674.0 | 45/4.22 | 7/2.81 | 8.44 | 33.80 | 2079.2 | 150.45 | 0.0459 |
| 630 | 13 | 630 | 79.80 | 710.0 | 54/3.85 | 19/2.31 | 44.60 | 34.70 | 2366.3 | 191.77 | 0.0459 |
| 710 | 7 | 710 | 49.10 | 759.0 | 45/4.48 | 7/2.99 | 8.96 | 35.90 | 2343.2 | 169.56 | 0.0407 |
| 710 | 13 | 710 | 89.90 | 800.0 | 54/4.09 | 19/2.45 | 12.30 | 36.80 | 2666.8 | 216.12 | 0.0407 |
| 800 | 4 | 800 | 34.60 | 835.0 | 72/3.76 | 7/2.51 | 7.52 | 37.60 | 2480.2 | 167.41 | 0.0361 |
| 800 | 8 | 800 | 66.70 | 867.0 | 84/3.48 | 7/3.48 | 10.40 | 38..30 | 2732.7 | 205.33 | 0.0362 |
| 800 | 13 | 800 | 101.00 | 901.0 | 54/4.34 | 19/2361 | 13.00 | 39.10 | 3004.9 | 243.52 | 0.0362 |
| 900 | 4 | 900 | 38.90 | 939.0 | 72/3.99 | 7/2.66 | 7.8 | 39.90 | 2790.2 | 188.33 | 0.0321 |
| 900 | 8 | 900 | 75.00 | 975.0 | 84/3.96 | 7/3.69 | 11.10 | 40.60 | 3074.2 | 226.50 | 0.0322 |
| 1000 | 4 | 1000 | 43.20 | 1043.0 | 72/4.21 | 7/2.80 | 8.41 | 42.10 | 3100.3 | 209.26 | 0.0289 |
| 1120 | 4 | 1120 | 47.30 | 1167.0 | 72/4.45 | 19/1.78 | 8.90 | 44.50 | 3464.9 | 234.53 | 0.0258 |
| 1120 | 8 | 1120 | 91.20 | 1211.0 | 84/4.12 | 19/2.47 | 12.40 | 45.30 | 3811.5 | 283.17 | 0.0258 |
| 1250 | 8 | 1250 | 102.00 | 1352.0 | 84/4.35 | 19/4.70 | 13.10 | 47.90 | 4253.9 | 316.04 | 0.0232 |
| 1250 | 4 | 1250 | 52.80 | 1303.0 | 84/4.70 | 19/1.88 | 9.40 | 47.00 | 3867.1 | 261.45 | 0.0231 |

AII-ALUMINIUM CONDUCTORS STEEL REINFORCED

ASTM B 232/B 232M-99                                           Table 9

ACSR

AMERICAN SIZES

OVERHEAD LINE CONDUCTORS

| Code Name | Area |  |  | Stranding & Wire Diameter |  | Overall Diameter | Weight | Breaking Load | DC Resistance | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Aluminium | Steel | Total | Auminium | Steel |  |  |  |  |  |
|  | mm² | mm² | mm² | mm | mm | mm | Kg/km | KN | Ohm/km | A |
| Turkey Swan Swanate Sparrow Sparate Robin Raven Quail Pigeon Penguin Waxwing Parridge Ostrich Linnet Oriole Chickadee Brant Ibis Lark Pelican Flicker Hawk Hen Osprey Parakeet Dove Eagle Peacock Squab Wood duck Teel Kingbird Rook Grosbeak Scoter Egret Flamingo Gannet Stilt Starling Redwing Tern Condor Cuckoo Drake | 13.29 21.16 21.16 33.61 33.61 42.39 53.48 67.42 85.03 107.23 135.16 135.16 152.00 170.45 170.45 201.42 201.42 201.42 201.42 241.68 241.68 241.68 241.68 282.00 282.00 282.00 282.00 306.58 306.58 306.58 306.58 322.26 322.26 322.26 322.26 322.26 337.74 337.74 362.58 362.85 362.58 402.84 402.84 402.84 402.84 | 2.21 3.55 5.35 5.61 8.52 7.10 8.90 11.23 14.19 17.87 7.48 22.00 24.77 27.74 39.81 11.16 26.13 32.77 46.97 1342 31.29 39.35 56.39 15.68 36.58 45.94 65.81 39.74 49.94 71.55 69.87 17.74 41.81 52.22 75.22 73.48 43.81 55.03 46.97 89.03 82.64 27.87 52.19 52.20 65.61 | 15.50 24.71 26.51 39.22 42.13 49.49 62.38 78.65 99.22 125.10 142.64 157.16 176.77 198.19 210.26 212.58 227.55 234.19 248.39 255.10 272.97 281.03 298.07 297.68 318.58 327.94 347.81 346.32 356.52 378.13 376.45 340.13 364.17 374.78 397.48 395.74 381.55 392.84 409.61 421.61 445.22 430.71 455.03 455.1 468.45 | 6/1.68 6/2.12 7/1.96 6/2.67 7/2.47 6/3.00 6/3.37 6/3.78 6/4.25 6/4.77 18/3.09 26/2.57 26/2.73 26/2.89 30/2.69 18/3.77 24/3.27 26/3.14 30/2.92 18/4.14 27/3.58 26/3.44 30/3.20 18/4.47 24/3.87 26/3.74 30/3.46 24/4.03 26/3.87 30/3.61 30/3.61 18/4.78 24/4.14 26/3.97 30/3.70 30/3.70 24/4.23 26/4.07 24/4.39 26/4.21 30/3.92 45/3.38 54/3.08 24/4.62 26/4.44 | 1/1.68 1/2.12 1/2.31 1/2.67 1/3.30 1/3.00 1/3.37 1/3.78 1/4.25 1/4.77 1/3.09 7/2.00 7/2.12 7/2.25 7/2.69 1/3.77 7/2.18 7/2.44 7/2.92 1/4.14 7/2.39 7/2.67 7/3.20 1/4.47 7/2.58 7/2.89 7/3.46 7/2.69 7/3.01 7/3.61 19/2.16 1/4.78 7/2.76 7/3.09 7/3.70 19/2.22 7/2.82 7/3.16 7/2.92 7/3.28 19/2.35 7/2.25 7/3.08 7/3.08 7/3.45 | 5.04 6.36 6.53 8.01 8.24 9.00 10.11 11.34 12.75 14.31 15.45 16.28 17.28 18.31 18.83 18.85 19.61 19.88 20.44 20.70 21.49 21.80 22040 22.35 23.22 23.55 24.21 24.20 24.51 25.25 25.24 23.88 24.84 25.15 25.88 25.90 25.40 28.30 26.31 26.68 27.43 27.03 27.72 27.74 28.11 | 53.6 85.3 99.6 135.7 158.7 171.1 216.1 272.0 343.00 432.7 430.2 545.9 613.4 687.5 783.3 641.3 761.0 812.4 925.2 769.7 913.5 975.1 1110.3 897.7 1065.6 1138.6 1295.6 1158.9 1237.0 1408.4 1396.6 1023.6 1217.6 1300.8 1480.7 1469.0 1276.6 1363.3 1370.4 1463.7 1650.6 1331.8 1520.7 1522.2 1626.4 | 5.2 8.3 10.5 12.7 16.1 15.8 19.4 23.6 29.5 37.1 30.6 50.3 56.5 62.7 77.0 44.2 64.9 72.5 90.3 58.5 76.1 86.7 105.9 60.9 88.1 100.5 123.7 95.6 106.8 128.5 133.4 69.4 101.0 112.1 134.8 140.1 105.4 117.4 113.4 126.3 153.9 98.3 125.4 124.1 140.1 | 2.15700 1.35600 1.35600 0.85300 0.85300 0.67650 0.53640 0.42550 0.33730 0.26760 0.21330 0.21420 0.19060 0.16990 0.17040 0.14320 0.14380 0.14380 0.14420 0.11930 0.11990 0.11990 0.22020 0.10220 0.10280 0.10280 0.10300 0.09449 0.09449 0.09473 0.09475 0.08942 0.08989 0.08989 0.09011 0.09012 0.08576 0.08576 0.07989 0.07992 0.08009 0.07192 0.07192 0.07190 0.07192 | 78 105 104 139 138 160 183 210 241 276 319 323 346 371 372 403 405 403 410 449 454 455 457 492 492 499 500 |
|  |  |  |  |  |  |  |  |  |  | 522 523 523 527 530 537 538 5.41 542 552 618 577 578 581 160 614 614 614 |

AII-ALUMINIUM CONDUCTORS STEEL REINFORCED

ASTM B 232/B 232M-99                                           Table 9 (Contd)

ACSR

AMERICAN SIZES

OVERHEAD LINE CONDUCTORS

| Code Name | Area |  |  | Stranding & Wire Diameter |  | Overall Diameter | Weight | Breaking Load | DC Resistance 20˚C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Aluminium | Steel | Total | Aluminium | Steel |  |  |  |  |  |
|  | mm² | m² | mm² | mm | mm | mm | Kg/km | Kn | Ohm/km | A |
| Mallard | 402.84 | 91387 | 494.71 | 30/4.14 | 19/2.48 | 28.96 | 1836.0 | 170.8 | 0.07208 | 618 |
| Ruddy | 456.06 | 31.45 | 487.35 | 45/3.59 | 7/2.40 | 28.73 | 1507.3 | 108.3 | 0.06356 | 656 |
| Canary | 456.06 | 59.10 | 515.16 | 54/3.28 | 7/3.28 | 29.52 | 1723.1 | 1413.9 | 0.06352 | 660 |
| Rail | 483.42 | 33.42 | 516.84 | 45/3.70 | 7/2.47 | 29.61 | 1598.1 | 115.2 | 0.05994 | 679 |
| Cardinal | 483.42 | 62.65 | 546.07 | 54/3.38 | 7/3.38 | 30.42 | 1825.9 | 150.3 | 0.05994 | 681 |
| Ortlan | 523.68 | 36.19 | 559.87 | 45/3.85 | 7/2.57 | 30.81 | 1730.5 | 123.2 | 0.05531 | 712 |
| Curlew | 523.68 | 67.87 | 591.55 | 54/3.51 | 7/3.51 | 31.68 | 1977.6 | 162.8 | 0.05531 | 715 |
| Bluejay | 563.39 | 93.03 | 602.96 | 45/4.00 | 7/2.66 | 31.96 | 1866.0 | 132.6 | 0.05161 | 743 |
| Finch | 563.93 | 71.48 | 635.41 | 54/3.65 | 19/2.19 | 32.85 | 2127.8 | 173.9 | 0.05161 | 746 |
| Bunting | 604.26 | 41.355 | 645.81 | 45/4.14 | 7/2.76 | 33.12 | 1996.9 | 141.9 | 0.0482 | 772 |
| Grackle | 604.26 | 76.52 | 680.78 | 54/3.77 | 19/2.27 | 33.97 | 2278.1 | 185.9 | 0.0482 | 773 |
| Bittern | 664.51 | 44.52 | 689.03 | 45/4.27 | 7/2.85 | 34.17 | 2130.8 | 151.7 | 0.04518 | 802 |
| Pheasant | 644.51 | 81.68 | 726.19 | 54/3.90 | 19/2.34 | 35.10 | 2431.4 | 193.9 | 0.04518 | 807 |
| Dipper | 684.84 | 47.10 | 732.26 | 45/4.40 | 7/2.93 | 35.16 | 2263.0 | 161.0 | 0.04259 | 831 |
| Martin | 684.84 | 86.71 | 771.55 | 54/4.02 | 19/2.41 | 36.17 | 2581.7 | 205.9 | 0.05259 | 835 |
| Bobolink | 725.16 | 50.32 | 775.48 | 45/4.53 | 7/3.02 | 36.24 | 2397.2 | 170.8 | 0.0416 | 859 |
| Plover | 728.16 | 91.81 | 816.97 | 54/2.48 | 19/2.48 | 37.24 | 2734.9 | 218.0 | 0.04016 | 862 |
| Nuthatch | 765.16 | 52.90 | 818.06 | 45/4.365 | 7/3.10 | 37.20 | 2529.6 | 178.4 | 0.03802 | 886 |
| Parrot | 765.16 | 97.16 | 862.32 | 54/4.25 | 19/2.55 | 38.25 | 2883.7 | 230.4 | 0.03802 | 890 |
| Lapwing | 805.8 | 55.48 | 861.28 | 45/4.78 | 7/3.18 | 38.16 | 2663.5 | 187.3 | 0.03612 | 911 |
| Falcon | 805.8 | 102.32 | 908.12 | 54/4.36 | 19/2.62 | 39.26 | 3038.5 | 242.9 | 0.03612 | 917 |
| Chukar | 901.93 | 73.55 | 975.48 | 84/3.70 | 19/2.22 | 40.70 | 3083.1 | 22832 | 0.03228 | 975 |

AII-ALUMINIUM CONDUCTORS STEEL REINFORCED

CSA  C  49  -  1965                                            Table  10

ACSR

CANADIAN SIZES

OVERHEAD LINE CONDUCTORS

| Code Name | Total Area |  |  | Stranding & Wire Diameter |  | Overall | Weight |  |  | Breaking Load | DC Resistance 20˚C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Auminium | Steel | Total | Aluminium | Steel | Total | Aluminium | Steel | Total |  |  |  |
|  | mm² | mm² | mm² | mm | mm | mm | Kg/km | Kg/km | Kg/km | kn | Ohm/km | A |
| Wren | 8.39 | 1.42 | 9.81 | 6/1.33 | 1/1.33 | 3.99 | 23 | 11 | 34 | 3.3 | 3.4226 | 63 |
| Warbler | 10.59 | 1.34 | 11.93 | 6/1.50 | 1/1.50 | 4.5 | 29 | 14 | 43 | 4.2 | 2.7139 | 67 |
| Turkey | 13.29 | 2.19 | 15.45 | 6/1.68 | 1/1.68 | 5.04 | 37 | 17 | 54 | 5.2 | 2.1535 | 86 |
| Thrush | 16.77 | 2.77 | 19.54 | 6/1.89 | 1/1.89 | 5.67 | 46 | 22 | 68 | 6.5 | 1.7.77 | 93 |
| Swan | 21.16 | 3.55 | 24.71 | 6/2.12 | 1/2.12 | 6.36 | 58 | 27 | 85 | 8.2 | 1.3537 | 109 |
| Swallow | 26.65 | 4.45 | 31.09 | 6/2.38 | 1/2.38 | 7.14 | 73 | 35 | 108 | 10.0 | 1.0738 | 126 |
| Sparrow | 33.61 | 5.61 | 39322 | 6/2.67 | 1/2.67 | 8.10 | 92 | 44 | 136 | 12.4 | 0.8504 | 140 |
| Robin | 42.39 | 7.10 | 49.49 | 6/3.00 | 1/3.00 | 9.00 | 116 | 55 | 171 | 15.5 | 0.6752 | 162 |
| Raven | 53.48 | 8.90 | 62.38 | 6/3.37 | 1/3.37 | 10.11 | 146 | 69 | 215 | 19.0 | 0.5351 | 186 |
| Quail | 67.42 | 11.23 | 78.65 | 6/3.78 | 1/3.78 | 11.34 | 185 | 88 | 273 | 10.8 | 0.4245 | 211 |
| Pigeon | 85.03 | 14.19 | 99.22 | 6/4.25 | 1/4.25 | 12.75 | 233 | 110 | 343 | 29.7 | 0.3366 | 241 |
| Penguin | 107.23 | 17.87 | 125.1 | 6/4.77 | 1/4.77 | 14.31 | 294 | 139 | 433 | 37.5 | 0.2671 | 276` |
| Owl | 135.16 | 17.55 | 152.71 | 6/5.36 | 7/1.74 | 16.90 | 371 | 137 | 508 | 42.5 | 0.2773 | 322 |
| Waxwing | 135.16 | 7.48 | 142.64 | 18/3.09 | 1/3.09 | 15.15 | 372 | 58 | 430 | 31.5 | 0.2126 | 319 |
| Partridge | 135.16 | 22.00 | 157.16 | 26/2.57 | 7.2.00 | 16.28 | 374 | 171 | 545 | 50.01 | 0.2136 | 321 |
| Pheobe | 152.00 | 8.45 | 160.45 | 18/3.28 | 1/3.28 | 16.40 | 418 | 65 | 483 | 35.5 | 0.1893 | 341 |
| Ostrich | 152.00 | 24.71 | 176.71 | 26/2.73 | 7/2.73 | 17.28 | 420 | 193 | 613 | 86.2 | 0.1900 | 343 |
| Piper | 152.00 | 35.48 | 187.48 | 30/2.54 | 7/2.54 | 17.78 | 420 | 277 | 697 | 68.6 | 0.1903 | 348 |
| Merlin | 170.45 | 9.48 | 179.93 | 18/3.47 | 1/3.47 | 17.35 | 469 | 74 | 543 | 39.8 | 0.1686 | 364 |
| Linnet | 170.45 | 27.81 | 198.26 | 26/2.89 | 7/2.25 | 18.31 | 470 | 217.0 | 687 | 62.5 | 0.1696 | 368 |
| Oriole | 170.45 | 39.81 | 210.26 | 30/2.69 | 7/2.96 | 18383 | 472 | 311.0 | 783 | 75.8 | 0.1696 | 370 |
| Chikadee | 201.42 | 11.16 | 212.58 | 18/3.77 | 1/3.77 | 18.85 | 555 | 86.0 | 641 | 469.3 | 0.1430 | 402 |
| Ibis | 201.42 | 32.77 | 234.19 | 26/3.14 | 7/2.44 | 19.88 | 557 | 256.0 | 813 | 72.0 | 0.1434 | 404 |
| Lark | 201.42 | 46.97 | 248.39 | 30/2.92 | 7/2.92 | 20.44 | 557 | 366.0 | 923 | 88.8 | 0.1437 | 410 |
| Pelican | 241.68 | 13.42 | 255.10 | 18/4.14 | 1/4.14 | 20.70 | 665 | 104.0 | 769 | 54.8 | 0.1191 | 449 |
|  | 241.68 | 23.74 | 265.42 | 22/3.74 | 7/2.08 | 21.20 | 667 | 186.0 | 853 | 68.6 | 0.1194 | 452 |
| Hawk | 241.68 | 39.42 | 281.10 | 26/3.44 | 7/2.67 | 21.77 | 667 | 308.0 | 978 | 86.5 | 0.1194 | 450 |
| Hen | 241.68 | 56.39 | 298.07 | 30/3.20 | 7/2.20 | 22.40 | 668 | 440.0 | 1108 | 103.9 | 0.1198 | 453 |
| Heron | 253.35 | 59.10 | 312.45 | 30/3028 | 7/3.28 | 22.96 | 701 | 461.0 | 1162 | 108.8 | 0.1142 | 469 |
| - | 282.00 | 27.68 | 309.68 | 22/4.04 | 7/2.24 | 22.88 | 777 | 216.0 | 993 | 79.10 | 0.1027 | 496 |
| Dove | 282.00 | 45.94 | 327.94 | 26/3.72 | 7/2.89 | 23.55 | 778 | 359.0 | 1137 | 79.10 | 0.1024 | 495 |
| Engle | 282.00 | 65.81 | 347.81 | 30/3.46 | 7/3.46 | 24.22 | 780 | 513.0 | 1293 | 121.2 | 0.1027 | 497 |
| - | 306.58 | 30.07 | 336.65 | 22/4.21 | 7/2.34 | 23.86 | 845 | 235.0 | 1080 | 84.9 | 0.0942 | 519 |
| Duck | 306.58 | 39.81 | 346.39 | 54/2.69 | 7/2.69 | 24. 21 | 848 | 311.0 | 1159 | 100.1 | 0.0945 | 520 |
| - | 322.26 | 31.61 | 35387 | 22/4.32 | 7/2.40 | 24.48 | 888 | 247.0 | 1135 | 84.8 | 0.0896 | 232 |
| Grosbeak | 322.26 | 52.45 | 374.71 | 26/3.97 | 7/3.09 | 25.15 | 890 | 409.0 | 1299 | 111.2 | 0.0896 | 530 |
| Egret | 322.26 | 73.55 | 395.81 | 30/3.70 | 19/2.22 | 25.90 | 891 | 576.0 | 1467 | 140.6 | 0.0896 | 542 |
| Goose | 322.26 | 41.74 | 364.00 | 54/2.78 | 7/2.76 | 24.84 | 891 | 326.0 | 1217 | 105.2 | 0.0899 | 534 |
| - | 337.74 | 17.35 | 355.09 | 42/3.20 | 7/1.78 | 24.54 | 933 | 135.0 | 1068 | 78.6 | 0.0856 | 546 |
| Gull | 337.74 | 43.81 | 381.55 | 54/2.28 | 7/2.82 | 25.38 | 935 | 342.0 | 1277 | 109.2 | 0.0856 | 553 |
| Starling | 362.58 | 59.03 | 421.61 | 26/4.21 | 7/3.28 | 26.68 | 1002 | 460.0 | 1462 | 125.0 | 0.0797 | 575 |
| Redwing | 362.58 | 82.58 | 445.16 | 30/3.92 | 19/2.35 | 27.43 | 1002 | 646.0 | 1648 | 153.9 | 0.0797 | 581 |
| - | 362.58 | 18.65 | 381.26 | 42/3.31 | 7/1.84 | 25.38 | 1002 | 146.0 | 1148 | 84.3 | 0.0797 | 573 |
| Crow | 362.58 | 46.97 | 409.55 | 54/2.92 | 7/2.92 | 26.28 | 1003 | 366.0 | 1369 | 117.2 | 0.0797 | 577 |
| Darke | 402.84 | 65.61 | 468.45 | 26/4.44 | 7/3.45 | 28.11 | 1112 | 512.0 | 1624 | 139.0 | 0.0715 | 611 |

AII-ALUMINIUM CONDUCTORS STEEL REINFORCED

CSA  C  49 – 1965                                        Table 10 (Contd)

CANADIAN SIZES

ACSR

OVERHEAD LINE CONDUCTORS

| Code Name | Total Area |  |  | Stranding & Wire Diameter |  | Overall Diameter | Weight |  |  | Breaking Load | DC Resisstance 20 C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Aluminium | Steel | Total | Aluminium | Steel | Total | Aluminium | Steel | Total |  |  |  |
|  | mm | mm | mm | mm | mm | mm | Kg/km | Kg/km | Kg/km | kn | Ohm/km | A |
| Mallard | 402.74 | 97.87 | 494.71 | 30/4.14 | 19/2.48 | 28.96 | 1113 | 719 | 1832 | 171 | 0.0719 | 618 |
|  | 402.84 | 20.71 | 423.55 | 42/3.50 | 7/1.94 | 26.82 | 1112 | 162 | 1274 | 93.6 | 0.0719 | 610 |
| Condor | 402.84 | 52.19 | 455.03 | 54/3.28 | 7/3.08 | 27.72 | 1113 | 408 | 1521 | 127 | 0.0719 | 615 |
|  | 443.10 | 22.84 | 465.94 | 42/3.67 | 7/2.04 | 28.14 | 1223 | 179 | 1402 | 101.6 | 0.0653 | 645 |
| Crane | 443.10 | 57.48 | 500.68 | 54/3.23 | 7/3.23 | 29.07 | 1226 | 448 | 1674 | 132.7 | 0.0653 | 649 |
|  | 456.06 | 23.42 | 479.48 | 42/3.72 | 7/2.07 | 28.53 | 1259 | 18.3 | 1442 | 104.5 | 0.0633 | 655 |
| Canary | 456.06 | 59.10 | 515.16 | 54/3.28 | 7/3.28 | 29.52 | 1262 | 462 | 1724 | 14307 | 0.0633 | 660 |
|  | 483.42 | 24.84 | 508.26 | 42/3.83 | 7/2.13 | 29.87 | 1335 | 193 | 1528 | 109 | 0.0597 | 678 |
| Cardinal | 483.42 | 62.65 | 546.07 | 54/3.38 | 7/3.38 | 30.42 | 1338 | 488 | 1826 | 152.3 | 0.0597 | 382 |
|  | 523.68 | 26397 | 550.65 | 42/3.99 | 7/2.21 | 30.57 | 1447 | 210 | 1657 | 118.1 | 0.0511 | 710 |
| Curlew | 523.68 | 67.87 | 591.55 | 54/3.21 | 7/3.51 | 31.59 | 1448 | 530 | 1978 | 165.2 | 0.0511 | 715 |
|  | 563.93 | 28.78 | 592.9 | 42/4.14 | 7/2.30 | 31.74 | 1557 | 226 | 1783 | 126.1 | 0.0512 | 741 |
| Finch | 563.93 | 71.55 | 636.48 | 54/3.65 | 19/2.19 | 32.85 | 1561 | 560 | 2121 | 178.8 | 0.0512 | 746 |
|  | 604.26 | 31.10 | 635.36 | 42/4.28 | 7/2.19 | 32.82 | 1668 | 243 | 1911 | 135.2 | 0.0479 | 772 |
| Grackle | 604.26 | 76.58 | 680.87 | 54/3.77 | 19/2.27 | 33.97 | 1671 | 600 | 2271 | 191.7 | 0.0479 | 776 |
|  | 644.51 | 33.16 | 677.67 | 42.4.42 | 7/2.46 | 33.9 | 1780 | 259 | 2039 | 144.3 | 0.0449 | 800 |
| Pheasant | 644.51 | 81.68 | 726.19 | 54/3.90 | 19/2.34 | 35.1 | 1783 | 638 | 2421 | 199.3 | 0.0449 | 805 |
|  | 684.84 | 35.23 | 720.07 | 42/4.56 | 7/2.53 | 34.95 | 1891 | 275 | 2166 | 153.2 | 0.0423 | 829 |
| Martin | 684.84 | 86.71 | 771.55 | 54/4.02 | 19/2.41 | 36.17 | 1894 | 679 | 2573 | 211.7 | 0.0423 | 835 |
|  | 725.10 | 37.35 | 762.45 | 42/4.69 | 7/2.61 | 35.97 | 2002 | 292 | 2294 | 162.4 | 0.0397 | 858 |
| Plover | 725.10 | 91.87 | 816.97 | 54/4.14 | 79/2.48 | 37.24 | 2006 | 719 | 2725 | 224.2 | 0.0400 | 862 |
|  | 765.35 | 39.35 | 804.7 | 42/4.82 | 7/2.67 | 36.93 | 2113 | 307 | 2420 | 171.2 | 0.0377 | 885 |
| Parrot | 765.35 | 96.84 | 860.19 | 54/4.25 | 19/2.55 | 38.25 | 2118 | 759 | 2577 | 237.1 | 0.0377 | 890 |
|  | 805.68 | 71.10 | 876.78 | 48/4.63 | 7/3.60 | 38.58 | 2225 | 554 | 2779 | 211.7 | 0.0358 | 929 |
| Falcon | 805.68 | 102.13 | 907.81 | 54/4.36 | 19/2.62 | 39.26 | 2229 | 799 | 3026 | 249.5 | 0.0358 | 917 |
|  | 805.68 | 34.84 | 840.52 | 72/3.77 | 7/2.52 | 37.72 | 2226 | 272 | 2498 | 175.7 | 0.0358 | 910 |

EXTRA HIGH STRENGTH STRANDINGS

| Bantam | 6.65 | 8.84 | 15.49 | 3/1.68 | 4/1.68 | 5.04 | 18.2 | 69.6 | 87.8 | 11.7 | 4.3218 | 61 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Magpie | 10.58 | 14.13 | 24.71 | 3/2.12 | 4/2.12 | 6.36 | 29.0 | 110.7 | 139.7 | 18.6 | 2.7077 | 77 |
| Shrike | 16.84 | 22.45 | 39.29 | 3/2.67 | 4/2.67 | 8.01 | 46.1 | 176.5 | 22.6 | 28.6 | 1.7054 | 99 |
| Snipe | 26.17 | 35.68 | 62.45 | 3/3.37 | 4/3.37 | 10.11 | 73.4 | 280.7 | 354.1 | 43.9 | 1.0718 | 132 |
| Loon | 33.68 | 44.97 | 78.65 | 3/3.78 | 4/3.78 | 11.34 | 92.4 | 353.4 | 445.8 | 55.3 | 0.8514 | 149 |
| Grouse | 40.52 | 14.13 | 54.65 | 8/2.54 | 1/4324 | 9.32 | 111.2 | 110.0 | 221.2 | 23.1 | 0.7077 | 157 |
| Petrel | 51.61 | 30.01 | 81.67 | 12/2.34 | 7/2.34 | 11.70 | 142.1 | 234.8 | 376.9 | 43.8 | 0.5591 | 193 |
| Minorca | 56.13 | 32.77 | 88390 | 12/2.44 | 7/2.44 | 12.20 | 55.6 | 255.7 | 311.3 | 4737 | 0.5134 | 192 |
| Leghorn | 68.19 | 39381 | 108.00 | 12/2.69 | 7/2.69 | 13.45 | 187.5 | 311.0 | 498.5 | 57.5 | 0.4226 | 221 |
| Guinea | 80.68 | 46.97 | 127.55 | 12/2.92 | 7/2.92 | 14.60 | 221.7 | 366.1 | 587.8 | 67.6 | 0.3579 | 244 |
| Dotterell | 89.48 | 52.19 | 191.67 | 12/3.08 | 7/3.08 | 15.40 | 247.0 | 407.8 | 654.8 | 73.0 | 0.3215 | 260 |
| Dorking | 96.71 | 56.39 | 153.10 | 12/3.20 | 7/3.20 | 16.00 | 266.4 | 490.5 | 706.9 | 78.9 | 0.2982 | 271 |
| Brahma | 102.97 | 91.87 | 194.84 | 16/2.86 | 19/2.48 | 18.12 | 285.7 | 718.8 | 1004.9 | 122.5 | 0.2815 | 287 |
| Auk | 102.84 | 92.32 | 195.16 | 8/4.05 | 7/2.25 | 14.83 | 282.7 | 217.3 | 500.0 | 49.6 | 0.2789 | 286 |
| Cochin | 107.10 | 62.45 | 169.55 | 12/3.37 | 7/3.37 | 16.85 | 297.7 | 488.1 | 782.8 | 87.4 | 0.2694 | 288 |

AII – ALUMINIUM CONDUCTORS STEEL REINFOCED

DIN 48 204 – APR 1984                                                 Table  11

GERMAN SIZES

ACSR

OVERHEAD LINE CONDUCTORS

| Area |  |  |  |  | Stranding & Wire Diameter |  | Overall Diameter | Weight |  |  | Breaking Load | DC Resistance at 20˚ c | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Aluminium | Steel | Aluminium | Steel | Total | Aluminium | Steel |  | Alminium | Steel | Total |  |  |  |
| mm | mm | mm | mm | mm | mm | mm | mm |  | Kg.km | Kg/km | kN | Ohm/km | A |
| 16 | 2.5 | 15027 | 2.54 | 17.8 | 6/1.80 | 1/1.80 | 5.4 | 42 | 20 | 62 | 5.81 | 1.8793 | 105 |
| 25 | 4 | 23.8 | 3.98 | 27.8 | 6/2.25 | 1/2.25 | 6.8 | 65 | 32 | 97 | 9.02 | 1.2028 | 140 |
| 35 | 6 | 34.35 | 5.73 | 40.1 | 6/2.70 | 1/2.70 | 8.1 | 94 | 46 | 140 | 12.70 | 0.8353 | 170 |
| 44 | 32 | 43.95 | 31.67 | 75.7 | 14/2.00 | 7/2.40 | 11.2 | 122 | 250 | 373 | 45.46 | 0.6573 |  |
| 50 | 8 | 48.25 | 8.04 | 56.3 | 6/3.20 | 1/3.20 | 9.6 | 132 | 64 | 196 | 17.18 | 0.5946 | 210 |
| 50 | 30 | 51.17 | 29.85 | 81.0 | 12/2.33 | 7/2.33 | 11.7 | 141 | 237 | 378 | 44.28 | 0.5644 |  |
| 70 | 12 | 69.89 | 11.40 | 81.3 | 26/1.85 | 7/1.44 | 11.7 | 193 | 91 | 284 | 26.31 | 0.4130 | 290 |
| 95 | 15 | 94.39 | 15.33 | 109.7 | 26/2.15 | 7/1.67 | 13.6 | 260 | 123 | 383 | 35.17 | 0.3058 | 350 |
| 95 | 55 | 96.51 | 56.30 | 152.8 | 12/3.20 | 7/3.20 | 16.0 | 266 | 466 | 714 | 80.20 | 0.2992 |  |
| 105 | 75 | 105.67 | 75.55 | 181.2 | 14/3.10 | 19/2.25 | 17.5 | 292 | 599 | 899 | 106.69 | 0.2736 |  |
| 120 | 20 | 121.57 | 19.85 | 141.4 | 26/2.44 | 7/1.90 | 15.5 | 336 | 158 | 494 | 44.94 | 0.2374 | 410 |
| 120 | 70 | 122.15 | 71.25 | 193.4 | 12/3.60 | 7/3.60 | 18.0 | 337 | 564 | 904 | 98.16 | 0.2364 |  |
| 125 | 30 | 127.92 | 29.85 | 157.8 | 30/2.33 | 7/2.33 | 16.3 | 353 | 238 | 590 | 57.86 | 0.2259 | 425 |
| 150 | 25 | 148.86 | 24.25 | 173.1 | 26/2.70 | 7/2.10 | 17.1 | 411 | 194 | 604 | 54.37 | 0.1939 | 470 |
| 170 | 40 | 171.77 | 40.08 | 211.9 | 30/2.70 | 7/2.70 | 18.9 | 475 | 319 | 494 | 77.01 | 0.1682 | 520 |
| 158 | 30 | 183.78 | 29.85 | 213.6 | 26/3.00 | 7/2.33 | 19.0 | 507 | 239 | 744 | 66.28 | 0.1571 | 535 |
| 210 | 35 | 209.06 | 34.09 | 243.2 | 26/3.20 | 7/2.49 | 20.3 | 577 | 273 | 848 | 74.94 | 0.1380 | 590 |
| 210 | 50 | 212.06 | 49.48 | 261.5 | 30/3.00 | 7/3.00 | 21.0 | 587 | 394 | 979 | 92.25 | 0.1363 | 610 |
| 230 | 30 | 230.91 | 29.85 | 260.8 | 24/3.50 | 7/2.33 | 21.0 | 638 | 239 | 874 | 73.09 | 0.1279 | 630 |
| 240 | 40 | 243.05 | 39.49 | 282.5 | 26/3.45 | 7/2.68 | 21.8 | 671 | 316 | 985 | 86.46 | 0.1188 | 645 |
| 265 | 35 | 263.76 | 34.09 | 297.8 | 24/3.74 | 7/2.49 | 22.4 | 728 | 274 | 998 | 82.94 | 0.1094 | 680 |
| 300 | 50 | 304.26 | 49.48 | 353.7 | 26/3.86 | 7/3.00 | 24.5 | 840 | 396 | 1233 | 105.09 | 0.0949 | 740 |
| 305 | 40 | 304.62 | 39.49 | 344.1 | 54/2.68 | 7/2.68 | 24.1 | 843 | 317 | 1155 | 99.30 | 0.0949 | 740 |
| 340 | 30 | 339.29 | 29385 | 369.1 | 48/3.00 | 7/2.33 | 25.0 | 983 | 242 | 1174 | 92.56 | 0.0851 | 790 |
| 380 | 50 | 381.70 | 49.48 | 431.2 | 54/3.00 | 7/3.00 | 27.0 | 1056 | 397 | 1448 | 120.91 | 0.0757 | 840 |
| 385 | 35 | 386.04 | 34.09 | 420.1 | 48/3.20 | 7/2.49 | 26.7 | 1067 | 277 | 1336 | 104.31 | 0.0748 | 850 |
| 435 | 55 | 434.29 | 56.3 | 490.6 | 54/3.20 | 7/3.20 | 28.8 | 1203 | 450 | 1647 | 136.27 | 0.0666 | 900 |
| 450 | 40 | 448.71 | 39*.49 | 488.2 | 48/3.45 | 7/2.68 | 28.7 | 1233 | 320 | 1553 | 120.19 | 0.0644 | 920 |
| 490 | 65 | 490.28 | 63.55 | 553.8 | 54/3.40 | 7/3.40 | 30.6 | 1356 | 510 | 1860 | 152.85 | 0.0590 | 960 |
| 550 | 70 | 549.65 | 71.25 | 620.9 | 54/3.60 | 7/3.60 | 32.4 | 1520 | 572 | 2085 | 167.42 | 0.0526 | 1020 |
| 560 | 50 | 561.70 | 49.48 | 611.2 | 48/3.86 | 7/3.00 | 32.2 | 1553 | 401 | 1943 | 146.28 | 0.0514 | 1040 |
| 680 | 85 | 678.58 | 85.95 | 764.5 | 54/4.00 | 19/2.40 | 36.0 | 1868 | 702 | 2564 | 209.99 | 0.0426 | 1150 |

Current rating:

Values are valid upto 60Hz, assuming wind velocity of 0.6 m/s, an initial temp. of 35˚ C due to the effect of solar radiation & a conductor final temp. of 80˚ C

ALL–ALUMINIUM ALLOY CONDUCTORS

AAAC

OVERHEAD LINE CONDUCTORS

This section deals with heat – treatable magnesium silicon type aluminium alloys to BS EN  50182, the electrical and mechanical properties of which all fall within the values suggested by publication 104 of the International Electro technical Commission, Conductors to all other recognized specifications can also be supplied. The alloys referred to have higher strength but lower conductivity than pure aluminium, Being lighter, alloy conductors can sometimes be used to advantage in place of the more conventionalACSR: Having lower breaking loads than the latter, their use becomes particularly favourable when ice and wind loading are low.

CONDUCTOR SECTIONS

ALL–ALUMINIUM ALLOY CONDUCTORS

BS EN 50182 : 2001                                                Table  12

AAAC

BRITISH SIZES

OVERHEAD LINE CONDUCTORS

| Old Code Name | Stranding & WireDiameter | Approximate Overall Diameter | Total Area | Weight | Breaking Load | DC Resistance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | mm | mm | mm² | Kg/Km | kN | Ohm/km | A |
| Box | 7/1.85 | 5.55 | 18.8 | 51.4 | 5.55 | 1.7480 | 93 |
| Acacia | 7/2.08 | 6.24 | 23.8 | 64.9 | 7.02 | 1.3828 | 110 |
| Almonda | 7/2.08 | 7.02 | 30.1 | 82.2 | 8.88 | 1.0926 | 132 |
| Cedar | 7/2.54 | 7.62 | 35.5 | 96.8 | 10.46 | 0.9273 | 132 |
| Deodar | 7/2.77 | 8.31 | 42.2 | 115.2 | 12.44 | 0.7797 | 148 |
| Fir | 7/2.95 | 8.85 | 47.8 | 130.6 | 14.11 | 0.6875 | 161 |
| Hazel | 7/3.30 | 9.90 | 59.9 | 163.4 | 17.66 | 0.5494 | 184 |
| Pine | 7/3.61 | 10.80 | 71.6 | 195.6 | 21.14 | 0.4591 | 204 |
| Holly | 7/3.91 | 11.70 | 84.1 | 229.5 | 24.79 | 0.3913 | 222 |
| Willow | 7/4.04 | 12.10 | 89.7 | 245.0 | 26.47 | 0.3665 | 233 |
| Oak | 7/4.65 | 13.95 | 118.9 | 324.5 | 35.07 | 0.2767 | 272 |
| Mulberry | 19/318 | 15.90 | 150.9 | 414.3 | 44352 | 0.2192 | 319 |
| Ash | 19/3.48 | 17.40 | 18037 | 496.1 | 53.31 | 0.1830 | 354 |
| Elm | 19/3.76 | 18.80 | 211.0 | 579.2 | 62.24 | 0.1568 | 385 |
| Poplar | 37/2.87 | 20.10 | 239.4 | 659.4 | 70.61 | 0.1387 | 414 |
| Sycamore | 37/3.23 | 22.60 | 303.2 | 835.2 | 89.40 | 0.1095 | 487 |
| Upas | 37/3.53 | 24.70 | 362.1 | 997.5 | 106.82 | 0.0917 | 527 |
| Yew | 37/4.06 | 28.40 | 479.0 | 1319.6 | 141.31 | 0.0693 | 629 |
| Totara | 37/4.14 | 29.42 | 498.1 | 1372.1 | 146.93 | 0.0666 | 640 |
| Rubus | 61/3.50 | 31.50 | 586.9 | 1622.0 | 173.13 | 0.0567 | 716 |
| Sorbus | 61/3.71 | 33.40 | 659.4 | 1822.5 | 194.53 | 0.0505 | 760 |
| Araucaria | 61/4.14 | 37.30 | 821.1 | 2269.5 | 242.24 | 0.0406 | 842 |
| Redwood | 61/4.56 | 41.00 | 996.2 | 2753.2 | 293.88 | 0.0334 | 920 |

AII-ALUMINIUM ALLOY CONDUCTOES

IEC  61089  (1991)                                               Table  13

AAAC

BRITISH SIZES

OVERHEAD LINE CONDUCTORS

| Code Number | Nominal Area | Stranding & Wire Diameter | Approx Overall Diameter | Approx Weight | Breaking Load | DC Resistance 20˚ C |
| --- | --- | --- | --- | --- | --- | --- |
|  | mm² | mm | mm | Kg/km | kN | Ohm/km |
| 16 | 18.4 | 7/1.83 | 5.49 | 50.4 | 5.43 | 1.7896 |
| 25 | 28.8 | 7/2.29 | 6.86 | 78.7 | 8.49 | 1.1453 |
| 40 | 46.0 | 7/2.89 | 8.68 | 125.9 | 13.58 | 50.7158 |
| 63 | 72.5 | 7/3.63 | 10.9 | 198.3 | 21.39 | 0.4545 |
| 1000 | 115 | 19/2.78 | 13.9 | 316.3 | 33.95 | 0.2877 |
| 125 | 144 | 19/3.10 | 15.5 | 395.4 | 42.44 | 0.2302 |
| 160 | 184 | 19/3.51 | 17.6 | 506.1 | 54.32 | 0.1798 |
| 200 | 230 | 19/3.93 | 1936 | 632.7 | 67.91 | 0.1439 |
| 250 | 288 | 19/4.39 | 22.0 | 790.8 | 84.88 | 0.1151 |
| 315 | 363 | 37/3.53 | 24.7 | 998.9 | 106.95 | 0.0916 |
| 450 | 518 | 37/4.22 | 29.6 | 1426.9 | 152.79 | 0.0641 |
| 500 | 575 | 37/4.45 | 31.2 | 1585.5 | 169.76 | 0.0577 |
| 560 | 645 | 61/3.67 | 33.0 | 1778.4 | 190.14 | 0.0516 |
| 630 | 725 | 61/3.89 | 35.0 | 2000.7 | 213.90 | 0.0458 |
| 710 | 817 | 61/4.13 | 37.2 | 2254.8 | 241.07 | 0.0407 |
| 800 | 921 | 61/4.38 | 39.5 | 2540.6 | 271.62 | 0.0361 |
| 900 | 1036 | 91/3.81 | 41.8 | 2861.1 | 305.58 | 0.0321 |
| 1000 | 1151 | 91/4.01 | 44.1 | 3179.0 | 339.53 | 0.0289 |
| 1120 | 1289 | 91/4.25 | 46.7 | 3560.5 | 380.27 | 0.0258 |
| 1250 | 1439 | 91/4.49 | 49.4 | 3973.7 | 424.41 | 0.0231 |

AII-ALUMINIUM ALLOY CONDUCTOES

ASTM B 399-97                                                   Table  14

AAAC

AMERICAN SIZES

OVERHEAD LINE CONDUCTORS

| Total Area |  | Stranding and WireDiameter | Overall Diameter | Weight | Breaking Load | DC Resistance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- |
| AWG or MCM* | mm² | mm | mm | Kg/km | kn | Ohm/km | A |
| 6 | 13.3 | 7/1.55 | 4.65 | 36.44 | 4.22 | 2.51900 | 67 |
| 4 | 21.1 | 7/1.96 | 5.88 | 57.89 | 6.72 | 1.58400 | 97 |
| 2 | 33.6 | 7/2.47 | 7.41 | 92.14 | 10.70 | 0.99580 | 128 |
| 0 | 53.5 | 7/3.12 | 9.36 | 146.50 | 17.00 | 0.62610 | 169 |
| 2/0 | 67.4 | 7/3.50 | 10.50 | 184.70 | 20.50 | 0.49680 | 194 |
| 3/0 | 85.0 | 7/3.93 | 11.79 | 232.70 | 25.90 | 0.39390 | 222 |
| 4/0 | 107.2 | 7/4.42 | 13.26 | 298.70 | 32.70 | 0.31240 | 256 |
| 250 | 126.7 | 19/2.91 | 14.55 | 346.90 | 39.00 | 0.26430 | 286 |
| 300 | 152.0 | 19/3.19 | 15.95 | 416.60 | 46.80 | 0.22040 | 319 |
| 350 | 177.3 | 19/3.45 | 17.25 | 485.50 | 52.30 | 0.18890 | 349 |
| 400 | 202.7 | 19/3.69 | 18.45 | 555.10 | 59.80 | 0.16550 | 378 |
| 450 | 228.0 | 19/3.91 | 19.55 | 624.40 | 67.30 | 0.14690 | 405 |
| 500 | 253.4 | 19/4.12 | 20.60 | 693.60 | 74.70 | 0.13220 | 431 |
| 550 | 278.7 | 37/3.10 | 21.70 | 762.90 | 93.90 | 0.12020 | 457 |
| 600 | 304.0 | 37/3.23 | 22.61 | 832.00 | 91.50 | 0.11010 | 481 |
| 650 | 329.4 | 37/3.37 | 23.59 | 901.30 | 95.00 | 0.10170 | 505 |
| 700 | 354.7 | 37/3.49 | 24.43 | 970.60 | 102.00 | 0.09439 | 527 |
| 750 | 380.0 | 37/3.62 | 25.34 | 1041.0 | 110.00 | 0.08816 | 549 |
| 800 | 405.4 | 37/3.73 | 26.11 | 1109.0 | 117.00 | 0.08260 | 570 |
| 900 | 456.0 | 37/3.96 | 27.72 | 1249.0 | 132.00 | 0.07341 | 610 |
| 1000 | 506.7 | 37/4.18 | 29.26 | 1388.0 | 146.00 | 0.06609 | 649 |

* Circular mils + 1000

AMERICAN SIZES

AII-ALUMINIUM ALLOY CONDUCTORS

Table 15

AAAC

OVERHEAD LINE CONDUCTORS

| Electrical Equivalent † Aluminium Area |  | Total Area |  | Stranding and Wire Diameter | Overall Diameter | Weight | Breaking Load | DC Resistance at 20˚C | Current |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AWG or MCM | mm | MCM | mm | mm | mm | Kg/km | kN | Ohm/km | A |
| 8 | 8.4 | 19 | 9.5 | 7/1.32 | 3.96 | 26 | 2.9 | 3.41600 | 55 |
| 7 | 10.6 | 24 | 12.0 | 7/1.48 | 4.44 | 33 | 3.6 | 2.71000 | 69 |
| 6 | 13.3 | 30 | 15.2 | 7/1.66 | 4.98 | 41 | 4.6 | 2.14800 | 79 |
| 5 | 16.8 | 38 | 19.1 | 7/1.86 | 5.58 | 52 | 5.8 | 1.70300 | 93 |
| 4 | 21.2 | 48 | 24.1 | 7/2.09 | 6.27 | 66 | 7.3 | 1.35200 | 108 |
| 3 | 26.7 | 60 | 30.4 | 7/2.35 | 7.05 | 83 | 9.2 | 1.07200 | 126 |
| 2 | 33.6 | 76 | 38.3 | 7/2.64 | 7.92 | 105 | 11.6 | 0.84940 | 139 |
| 1 | 42.4 | 95 | 48.3 | 7/2.96 | 8.88 | 132 | 14.7 | 0.67420 | 161 |
| 1/0 | 53.5 | 120 | 61.0 | /7/3.33 | 9.99 | 166 | 18.5 | 0.53440 | 186 |
| 2/0 | 67.4 | 152 | 76.8 | 7/3.74 | 11.22 | 210 | 23.3 | 0.42380 | 211 |
| 3/0 | 85.0 | 192 | 97.0 | 7/4.20 | 12.60 | 265 | 29.4 | 0.33550 | 242 |
| 4/0 | 107.2 | 241 | 122.3 | 7/4.72 | 14.15 | 334 | 37.1 | 0.26660 | 276 |
| 4/0 | 107.2 | 241 | 122.3 | 19/2.86 | 14.30 | 335 | 37.1 | 0.26780 | 280 |
| 266.8 | 135.2 | 304 | 154.1 | 19/3.21 | 16.05 | 423 | 46.7 | 0.21250 | 321 |
| 300.0 | 152.0 | 342 | 173.4 | 19/3.41 | 17.05 | 475 | 52.6 | 0.18890 | 343 |
| 336.0 | 170.5 | 384 | 194.4 | 19/3.61 | 18.05 | 533 | 58.9 | 0.16840 | 396 |
| 397.5 | 201.4 | 453 | 229.7 | 19/3.92 | 19.60 | 629 | 69.7 | 0.14230 | 404 |
| 477.0 | 241.7 | 544 | 275.7 | 19/4.30 | 21.50 | 756 | 83.6 | 0.11870 | 451 |
| 500.0 | 253.3 | 570 | 288.8 | 37/3.15 | 22.05 | 796 | 87.6 | 011370 | 464 |
| 556.5 | 282.0 | 635 | 321.5 | 37/3.33 | 23.31 | 885 | 97.4 | 0.10260 | 497 |
| 636.0 | 322.3 | 725 | 367.4 | 37/3.56 | 24.92 | 1012 | 111.4 | 0.08950 | 533 |
| 715.5 | 362.5 | 816 | 413.7 | 37/3.77 | 26.39 | 1140 | 125.4 | 0.07950 | 577 |
| 750.0 | 380.0 | 856 | 433.7 | 37/3.86 | 27.02 | 1195 | 131.4 | 0.07580 | 594 |
| 795.0 | 402.8 | 907 | 459.4 | 37/3.98 | 27.86 | 1266 | 139.2 | 0.07140 | 614 |
| 814.5 | 443.1 | 997 | 505.2 | 37/4.16 | 29.12 | 1391 | 153.2 | 0.06500 | 648 |

* Circular mils × 1000

† Auminium conductors with electrical properties complying with CSA C49-1957

AII-ALUMINIUM ALLOY CONDUCTORS

DIN  48 201 Part  6  1981                                               Table  16

AAAC

GERMAN SIZES

OVERHEAD LINE CONDUCTORS

| Total Area |  | Stranding and Wire Diameter | Overall Diameter | Weight | Breaking Load | DC Resistance at 20˚ C | Current Rating |
| --- | --- | --- | --- | --- | --- | --- | --- |
| mm² | mm² | mm | mm | Kg/km | kN | Ohm/km | A |
| 16 | 15.890 | 7/1.70 | 5.1 | 43 | 4.44 | 2.09100 | 105 |
| 25 | 24.250 | 7/2.10 | 6.3 | 66 | 6.77 | 1.37200 | 135 |
| 35 | 34.360 | 7/2.50 | 7.5 | 94 | 9.60 | 0.96700 | 170 |
| 50 | 49.480 | 7/3.00 | 9.0 | 135 | 13.82 | 0.67160 | 210 |
| 50 | 48.350 | 19/1.80 | 9.0 | 133 | 13.50 | 0.68930 | 210 |
| 70 | 65.821 | 19/2.10 | 10.5 | 181 | 18.38 | 0.50790 | 255 |
| 95 | 93.270 | 19/2.50 | 12.5 | 256 | 26.05 | 0.35800 | 320 |
| 120 | 116.990 | 19/2.80 | 14.0 | 322 | 32.68 | 0.28530 | 365 |
| 150 | 147.110 | 37/2.25 | 15.8 | 406 | 41.09 | 0.22780 | 425 |
| 185 | 181.620 | 37/2.50 | 17.5 | 500 | 50.73 | 0.18420 | 490 |
| 240 | 242.540 | 61/2.25 | 20.3 | 670 | 67.74 | 0.13850 | 585 |
| 300 | 299.430 | 61/2.50 | 22.5 | 827 | 83.63 | 0.11190 | 670 |
| 400 | 400.140 | 61/2.89 | 26.0 | 1104 | 111.76 | 0.08407 | 810 |
| 500 | 499.830 | 61/3.23 | 29.1 | 1379 | 139.60 | 0.06713 | 930 |
| 625 | 626.200 | 91/2.69 | 32.6 | 1732 | 174.90 | 0.05375 | 1075 |
| 800 | 802.090 | 91/3.35 | 36.9 | 2218 | 224.02 | 0.04197 | 1255 |
| 1000 | 9993.710 | 91/3.74 | 41.1 | 2767 | 279.22 | 0.03360 | 1450 |

Current rating values valid upto 60Hz with a wind speed of 0.6 m/s influence giving ambient initial temperature of 35˚C and final temperature of 80˚C: